[image: image10.wmf]
THE REGULATORY REFORM (FIRE SAFETY) ORDER 2005

FIRE RISK ASSESSMENT

INTRODUCTION
The Regulatory Reform (Fire Safety) Order 2005 (RR (FS) O) replaces previous fire safety legislation.  Any Fire Certificate issued under The Fire Precautions Act 1971 ceases to have any effect from the introduction of the RR(FS)O, and the Fire Precautions (Workplace) Regulations 1997 (amended 1999), which represented a significant shift of emphasis of the law towards Risk Assessment, are also revoked by the new Order.

If you have previously conducted a Fire Risk Assessment under the Fire Precautions (Workplace) Regulations, and this assessment has been regularly reviewed, then all you will need to do now is perform a further review, taking into account those issues not covered by previous legislation.

INDEMNITY
This document has been produced as a tool to assist you in completing a fire risk assessment of your premises.  It is used entirely at your own risk to identify what you consider are your significant findings, and also whether you consider the information therein to be suitable and sufficient.  It is in no way exhaustive, and Northumberland Fire & Rescue Service accepts no liability for any circumstances which may arise as a result of using this tool.

FURTHER ASSISTANCE & REFERENCE
A set of Guides are available (listed below) to assist you in what you have to do to comply with fire safety law, help you to carry out a fire risk assessment and identify the general fire precautions you need to have in place.  They are designed so that a responsible person, with limited formal training or experience, should be able to perform this task.  If you read the Guide and decide you are unable to apply the guidance then you should seek expert advice.

More complex premises will probably need to be assessed by a person who has a comprehensive knowledge and training or experience in fire risk assessment.

Guide 1
Office and Shops
Guide 2

Factories and Warehouses
Guide 3

Sleeping Accommodation
Guide 4

Residential Care Premises
Guide 5

Educational Premises
Guide 6

Small and Medium Places Of Assembly
Guide 7

Large Places of Assembly
Guide 8

Theatres and Cinemas
Guide 9

Outdoor Events
Guide 10

Healthcare Premises
Guide 11

Transport Premises and Facilities
Should you require further guidance, contact your local Fire Safety Officer via (01670) 621140.
THE REGULATORY REFORM (FIRE SAFETY) ORDER 2005
FIRE RISK ASSESSMENT

	PREMISES DETAILS

	Name:
	Barrasford Village Hall

	Address:
	Barrasford

	
	Hexham

	
	Northumberland

	Postcode:
	NE48 4AA

	Occupancy Times
	Varied


	FIRE ORGANISATION

	Responsible Person
	The Committee

	Fire Co-ordinator
	N/A

	Fire Wardens
	N/A

	Nominated users of fire-fighting equipment
	Varied – trained in operation of water extinguishers

	Person responsible for the fire alarm system
	None fitted. Weekly testing of detectors by competent person recorded on site.

	Confirmation that FIRE forms part of the premises safety policy
	Yes – as detailed within village hall policy / mandate

	Other responsible persons (in multi-occupied buildings)
	N/A


	Assessment completed by:
	Mr I Stewart

	Date Initial assessment completed:
	27.08.2012

	Signature:
	I.Stewart


The Assessment will be reviewed annually or sooner if alterations or changes in the activity are carried out or planned.

	ASSESSMENT REVIEW

	DATE
	SATISFACTORY

YES/NO
	NAME
	SIGNATURE

	30th April 21
	Yes
	Michelle Nixon
	M Nixon

	6th May 25
	 Yes
	Richard Haycock
	   R Haycock  

	
	
	
	

	
	
	
	


SECTION 1 - HAZARD IDENTIFICATION

1.1
COMBUSTIBLE/OXIDISING MATERIALS

	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	1.1
Are highly flammable materials or gases stored?

If Yes, is storage in accordance with current legislation/guidance?
(List materials at Appendix A)
	
	(
	

	1.2
Are excessive quantities of combustible materials displayed or stored?


	
	(
	

	1.3
Are there any other readily combustible materials stored/used that represent a significant hazard?

If Yes, is storage in accordance with current legislation/guidance?

(List materials at Appendix A)
	
	(
	

	1.4
Is combustible waste allowed to accumulate?


	
	(
	Waste bins supplied are satisfactory and located outside of the building..

	1.5
Are substantial areas of walls or ceilings covered with flammable linings?


	(
	
	Wooden cladding to walls of main hall that will increase the fire loading in the event of a fire. This forms part of the risk assessment and on site personnel are aware to its presence. No naked flames or ignition sources present. Long term replacement plan. Smoke detector and extinguisher present, supported by evacuation plan and suitable / sufficient exits.

	1.6
Is oxygen or oxidising agents stored or used?
If Yes is storage in accordance with current legislation/guidance?

(List materials at Appendix A)
	
	(
	

	1.7
Where dangerous substances are present, can these be eliminated, reduced or replaced by a less dangerous substance?
	(
	
	Asbestos panels in ceiling within supper room – have been removed


	REMARKS:
	
	
	

	
	
	
	Asbestos encased in the walls of the supper room. RH 6/5/25


1.2
SOURCES OF IGNITION
	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	1.8
Does the work activity involve processes such as cooking, welding, flame cutting or frictional heat?
	(
	
	Within kitchen area only – cooker, toaster and microwave present and operated only when qualified / competent personnel present. Only for specific events.

	1.9
Does the Workplace have gas or oil burning equipment?
	
	(
	Electric heating only.

	1.10
Are there light bulbs and fittings near flammable materials?
	
	(
	

	1.11
Is electrical equipment or wiring faulty or damaged?
	
	(
	Recent wiring in most parts of the building. Forms part of the quarterly building checks.

	1.12
Does the electrical equipment have extension leads?
	(
	
	Only when events are taking place – normally supplied by external entertainers. Committee to ensure required testing and maintenance, certification by all visiting personnel / parties using electric sockets - to be recorded within building log book.

	1.13
Are there multi point adaptors in electrical sockets?
	
	(
	

	1.14
Are all items of portable electrical equipment inspected regularly (PAT test) and fitted with correctly rated fuses?
	
	(
	To be considered by committee as an action point – to be recorded within building log book

	1.15
Is the wiring of the electrical installation inspected periodically by a competent person?
	
	(
	To be considered and implemented by committee – to be recorded within building log book.

	1.16
Are there portable heaters – are they fitted with suitable guards kept unobstructed and secured?
	(
	
	Used only a strictly limited basis and under the direction of a competent person.

	1.17
Is arson a potential problem?
	
	(
	

	1.18
Are there any other sources of ignition in the workplace?  If yes, what are they?
	
	(
	Only accidental source of ignition remains electrical on site or as a result of deliberate act. No smoking on site. No pyrotechnics. No naked flames.

	REMARKS:
	
	
	

	
	
	
	1.18 Solar system batteries in annex to main hall (2025) Warning notice posted.
1.14 Annual PAT test carried out by WNCBC 
1.15 Yes this is a requirement of the building insurance

RH 6/5/2025



SECTION 2 - PEOPLE AT RISK

	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	2.1
Do any members of staff work in areas where there is a high risk of a fire occurring?

If yes, have they been trained:-
· Appropriately for the hazards?

· In the action to take in the event of fire?
	
	(
	No members of staff present. Activity coordinators / responsible person[s] when activities are being undertaken on site.
Committee of responsible personnel [all listed] who induct on site a nominated person prior to room booking. Recorded within building log book.  

	2.2
Are the premises used regularly by people with impaired mobility?  If yes:-
· Is the number of trained staff adequate to ensure safe evacuation?

· Are the escape routes suitable for the people who have to use them?
	
	(
	Escape routes remain suitable for any person with impaired mobility.

	2.3
Do people sleep in the premises?  If yes:-
· Is an automatic fire alarm fitted?

· Are arrangements in place to ensure that all sleeping areas are evacuated?
	
	(
	

	2.4
Are young persons employed?  If yes:-
· Have they been adequately trained?

· Are they adequately supervised?
	
	(
	

	2.5
Do unsupervised minors or a large number of minors frequent the premises?  If yes:-
· Is there a sufficient number of trained staff on duty?

· Are members of staff trained in evacuation procedures for the minors?
· Are procedures in place to inform and reunite parents to minors during an evacuation?

· Are procedures in place to ensure the premises are fully evacuated?
	(
	
	Toddler groups and party’s – adult supervision at all times normally on a 1:1 basis. Voluntary groups without staff, utilising the community facility as a meeting place.
Presence of a responsible person who has undertaken the site familiarisation / induction and they are recorded within building log book. Confirmed on an annual basis.

Yes


SECTION 2 - PEOPLE AT RISK (Continued)

	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	2.6
Could a fire in the premises affect persons in the immediate vicinity?  If yes:-
· Consider the effect of hazardous substances, are they stored and used in accordance with national guidance?

· Consider the impact of compressed gas cylinders, are they stored safely in accordance with national guidance?

· Are warning systems for the public in place where necessary?

· Are evacuation plans for the public in place where necessary?

· Could any products used in the buildings construction affect persons in the vicinity during a fire?

· Could a fire spread to adjacent properties placing persons at risk?
	(

	(
	Presence of asbestos

	2.7
Are contractors and maintenance workers made aware of the establishment’s emergency procedure and the dangers posed by fire?
	(
	
	

	2.8
Does anyone work alone or in remote parts of the premises?
	
	(
	No work undertaken

	2.9
Is there more than one building forming part of the concerns holding?  If Yes:-
· Where necessary, has procedures been put in place to account for all persons during an emergency?

· Is it necessary to have linked fire alarm systems?
	
	(
	Appointed person to verify all areas are clear and vacated

	REMARKS:
	
	
	

	
	
	
	2.5
Toddler Group no longer meets in Barrasford Village hall

Barrasford Scout Group utilise the facility with responsible persons who have undertaken the site familiarisation / induction. RH  6/5/2025


SECTION 3 - MEANS OF ESCAPE
	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	3.1
Has the premises been built, and any alterations since, been carried out in accordance with the Building Regulations?

If No, do the premises conform to recognised national guidance regarding means of escape?

(It may be necessary to consult with the Fire Safety Officer to confirm that the premises are satisfactory)
	(
	
	

	3.2
Is there an alternative exit from the premises?

N.B. Where a “dead-end condition” exceeds 18m consult the Fire Safety Officer.
	(
	
	

	3.3
Do exits lead to a place of safety? (Not an enclosed room)
	(
	
	

	3.4
Are all gangways and escape routes free from obstructions?
	(
	
	

	3.5
Are the escape routes free from tripping and slipping hazards?
	(
	
	

	3.6
Are steps and stairs in a good state of repair?
	(
	
	

	3.7
Are all fire resisting doors clearly indicated by a suitable sign?
	(
	
	

	3.8
Are all fire doors fitted with intumescent strips and cold smoke seals?
	
	(
	To be reviewed by the committee

	3.9
Are self closing devices on fire resisting doors working efficiently?
	(
	
	Inspected on a regular basis

	3.10
Are all fire exit doors easily opened without the use of a key?
	(
	
	As above

	3.11
Is there a notice indicating the method of operating any panic fastening on fire doors?
	
	N/A
	

	3.12
Are all exits clearly indicated with the “running man” sign?
	(
	
	

	3.13
Are all fire doors and final exit doors checked on a monthly basis?
	(
	
	Refer to log book


SECTION 3 - MEANS OF ESCAPE (Continued)

	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	3.14
Are the results of tests/maintenance recorded in the Fire Log Book?
	(
	
	

	REMARKS:
	
	
	

	
	
	
	3.8 and 3.9

N/A Not applicable as all fire exit doors are final exit doors to the exterior of the building
3.10

All fire exit doors open without a key
RH 6/5/253



SECTION 4 - LIGHTING/EMERGENCY LIGHTING
	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	4.1
Is there adequate lighting on fire exit routes?
	(
	
	

	4.2
Are the premises used during the hours of darkness?
	(
	
	

	4.3
Are their any areas devoid of natural lighting (windowless)?
	(
	
	

	4.4
Where 4.2 and 4.3 is Yes, is emergency lighting provided?
	(
	
	

	4.5
Where 4.4 is Yes, is it installed and maintained in accordance with current guidance (BS5266: Part1)?
	(
	
	

	4.6
Are the results of tests/maintenance recorded in the Fire Log Book?
	(
	
	

	REMARKS:
	
	
	

	
	
	
	4.4
Emergency lighting is required in the disabled toilet. Committee to address

RH 6/5/2025




SECTION 5 - FIRE WARNING
	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	5.1
Is a suitable means of raising the alarm in case or fire provided?
	(
	
	

	5.2
Is the means of raising the alarm in case of fire clearly audible throughout the premises?
	
	(
	Battery and mains operated detectors 

	5.3
Can the fire alarm be raised without placing anyone in danger?

N.B No one should travel more than 30m to reach a call point.
	(
	
	This detail forms part of the ‘Hire Agreement’.

	5.4
Are the fire alarm call points clearly visible, unobstructed and suitably indicated?
	
	(
N/A
	

	5.5
Do the premises provide sleeping accommodation?
	
	(
	

	5.6
Could a fire develop un-noticed?
	(
	
	

	5.7
If the answer to 5.5 or 5.6 is yes, are the premises provided with automatic fire detectors?
	(
	
	

	5.8
Where an electrical fire alarm system is provided, is it installed and maintained in accordance with current guidance  (BS5839: Part 1 (or Part 6 where appropriate))
	
	
	N/A

	5.9
Is the fire alarm tested by the user on a weekly basis?
	(
	
	

	5.10
Are the results of tests/maintenance recorded in the Fire Log Book?
	
	(
	To be undertaken weekly and recorded

	REMARKS:
	
	
	

	
	
	
	5.2
All mains operated detectors
RH 6/5/2025


SECTION 6 - FIRE FIGHTING EQUIPMENT
	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	6.1
Are hose reels provided?  If yes have they been serviced within the last 12 months?
	
	(
	

	6.2
Are portable fire extinguishers suitably located and available to use for general fire-fighting purposes?

a. 1 x 9 litre water or 1 x 6 litre AFFF extinguisher for each 200 m2 of floor area or part thereof.

b. No one should have to travel more than 30m to reach an extinguisher
	(
(
(
	
	Only to be used by trained personnel – building operates an evacuation policy, stay out and get the fire service out. Doors closed where possible on exit.

	6.3
Are appropriate fire extinguishers provided for special fire risks e.g. electrical, oil etc?
	
	(
	Water only
Fire blanket provided

	6.4
Are fire extinguishers located in conspicuous positions, with the carrying handle about 1m from the floor?
	(
	
	

	6.5
Does the position of the fire extinguishers need to be indicated?
	(
	
	

	6.6
Has each fire extinguisher been serviced within the last 12 months?
	(
	
	

	6.7
Have a sufficient number of staff members been nominated and trained in the use of the fire fighting equipment provided?
	
	(
	

	6.8
Where necessary, has an automatic fire suppression system been installed?
	
	(
	

	REMARKS:
	
	
	

	
	
	
	


SECTION 7 – FIRE-FIGHTER PROVISIONS

	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	7.1
Are luminous discharge tube signs provided?

If Yes, has a Fire-fighters switch been provided and installed in accordance with national guidance?
	(
	(
	

	7.2
Are any facilities, equipment or devices provided for the use of or the protection of fire-fighters? E.g. rising mains, fire-fighting lobbies, smoke extraction systems etc.

If Yes, please list
	
	(
	

	7.3
If 7.2 is Yes, are they subject to routine maintenance, in working order and in good repair?
	
	
	

	REMARKS:
	
	
	

	
	
	
	


SECTION 8 - FIRE ACTION
	CONSIDERATION
	YES
	NO
	ACTION REQUIRED

	8.1
Are Fire Action Notices displayed at each fire alarm call point?  (See Appendix C)
	(
	
	Main Hall

	8.2.
Would all staff know what to do on discovery of a fire?
	(
	
	No staff – users of the facility are aware
This detail forms part of the ‘Hire Agreement’.

	8.3.
Would all staff know the action to take when the fire alarm sounds?
	(
	
	This detail forms part of the ‘Hire Agreement’.

	8.4.
Do all staff know where their assembly point is?
	(
	
	This detail forms part of the ‘Hire Agreement’.

	8.5
Has an emergency plan been drawn up in case of a major fire?
	
	(
	

	8.6
Is a copy of the emergency plan kept in a place other than at the workplace where it can be quickly obtained in an emergency?
	
	(
	

	8.7
Has the significant findings from the fire risk assessment been communicated to all staff?
	(
	
	Discussed with the committee and considered for inclusion during on site induction

	8.8
Has any significant hazards been communicated to the Fire Authority?  (See appendix B)
	
	
	None identified

	8.9
In premises with more than one occupier, has suitable arrangements been established to co-operate and co-ordinate safety measures between responsible persons?
	
	
	N/A

	REMARKS:
	
	
	

	
	
	
	8.7
Discussed with the committee

Included in Hire Agreement

RH 6/5/25


Appendix A
REGISTER OF HIGHLY FLAMMABLE, DANGEROUS SUBSTANCE, OXYGEN OR
OXIDISING AGENT MATERIAL STORED OR USED ON THE PREMISES
	MATERIAL
	LOCATION
	MAXIMUM QUANTITY STORED OR USED

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


Appendix B

	FIRE HAZARD NOTIFICATION

	From:
	

	
	

	
	

	
	

	
	

	Date:
	

	Contact:
	

	Telephone Number:
	

	To:
	Chief Fire Officer

Northumberland Fire and Rescue Service

West Hartford Business Park
West Hartford

CRAMLINGTON

Northumberland

NE61 3JP

	Dear Sir



	Re:
Fire Risk Assessment

Regulatory Reform (Fire Safety) Order 2005

Notification of Significant Fire Hazard within the Premises detailed Premises:-

	The following was considered to be a significant fire hazard within the premises.  Therefore special procedures may be necessary for rescue work and fire-fighting.

	

	Signed

Print Name
	


[image: image1.jpg]Barrasford Village Hall

HRNENEN

Station Road, Barrasford, Hexham, NE48 4AA
Registered Charity no. 1051443



[image: image3.png]



[image: image4.png]



[image: image5.wmf][image: image6.wmf]
[image: image7.wmf]
[image: image8.wmf]
[image: image9.wmf]





FIRE RISK ASSESSMENT – RECORD OF SIGNIFICANT FINDINGS

	Fire Risk Assessment for: Barrasford Village Hall


	Company:


	

	Address:


	

	
	

	
	


	Assessment undertaken by Ian Stewart


	Date
	28.10.12                   6.5.25

	Completed by
	Ian Stewart              Richard Haycock

	Signature
	I.Stewart                  R Haycock


	Step 1 – Identify Fire Hazards



	Sources of Ignition
	Sources of Fuel
	Sources of Oxygen

	Electricity 
	Wood panelling
	Outside air

	
	Building structure
	

	
	
	

	
	
	


	Step 2 – People at Risk



	Users of the facility

	

	

	


	Step 3 – Evaluate, remove, reduce and protect from risk



	3.1
Evaluate the risk of fire occurring
	Low

	3.2
Evaluate the risk to people from a fire starting in the premises
	Low

	3.3
Remove and reduce the hazards that may cause a fire
	As highlighted within document

	3.4
Remove and reduce the risks to people from a fire
	No smoking, No naked flames, PAT tested electrical apparatus only, supervised use of the kitchen


	Step 5 - Assessment Review



	Assessment review date
	Completed by
	Signature

	6/5/2025
	Richard Haycock
	R Haycock

	Review Outcome (where substantial changes have occurred a new record sheet should be used

	Please see comments under Remarks of each section.


[image: image2.png]



Appendix C





FIRE





A person discovering a fire should:-





Raise the fire alarm immediately by breaking the glass of the nearest fire alarm call point.





Call for assistance and, if safe to do so, the trained persons named below may attempt to tackle the fire with the appliances provided.




















On hearing the alarm:


The Fire and Rescue Service should be called immediately by:














Leave the building in an orderly manner by the nearest exit 


and report to the assembly point at:-








If possible, switch off all machines and close doors and windows as you leave the building





�





�





Dial 999





Dialling 999 and giving the call distinctly as: 


Barrasford Village Hall, Station Road, Barrasford, NE48 4AJ





ENTRANCE TO CHOLLERTON FIRST SCHOOL 





Do not stop to collect personal belongings


Do not re-enter the building until instructed to do so








18

